## HCVR-3 Calculator Tool
HCVR-3 Battery Calculator Tool
Hochiki America Corporation
[13 empty] | Yes | 0 | 0
[13 empty] | No | 1 | 1
This tool is designed to help you confirm the performance of the HCVR-3 panel during AC power fail conditions. | [13 empty] | 2 | 2
[14 empty] | 3 | 3
[14 empty] | 4 | 4
Please Note: | [13 empty] | 5 | 5
- The maximum standby capability of the HCVR-3 is 24 hours. The maximum alarm time is 5 minutes. | [13 empty] | 6 | 6
- The total standby current may not exceed 236 mA. | [13 empty] | 7 | 7
- The total alarm current may not exceed 2.0 amps. | [13 empty] | 8
- The maximum battery size is 7Ah. | [13 empty] | 9
- This calculation includes maximum standby and alarm current for zones 1 - 3. | [13 empty] | 10
- This calculation includes 20% battery derating. | [13 empty] | 11
12
[5 empty] | Instructions: Enter information for your system in the blue cells below. | [8 empty] | 13
14
[7 empty] | Standby | Alarm |  | standby | alarm |  |  | 15
|  |  | HCVR-3 Control Panel |  | 1 |  | 0.1 | 0.62 | [5 empty] | 16
|  |  | HCVR-SDU Status Display Unit |  | 0 |  | 0 | 0 |  | 0.05 | 0.094 |  |  | 17
|  |  | HCVR-AB Ancillary Board |  | 0 |  | 0 | 0 |  | 0.016 | 0.175 |  |  | 18
|  |  | HCVR-SQA Sequential Activator |  | 0 |  | 0 | 0 |  | 0.006 | 1 |  |  | 19
If SQA units are to be used, enter only the number of SQA units and leave the Exting Circuit Alarm Current at zero.
20
|  |  | NAC 1 Alarm Current: |  | 0 |  |  | 0
|  |  | NAC 2 Alarm Current: |  | 0 |  |  | 0
|  |  | NAC 3 Alarm Current: |  | 0 |  |  | 0
|  |  | Exting Circuit Alarm Current: |  | 0 |  |  | 0
[6 empty] | Totals: | 0.1 | 0.62
Please Note:
-The AUX 24V connection on the HCVR-3 is only for providing 24V to the HCVR-AB and/or HCVR-SQA modules.
- The Status Units Power connection on the HCVR-3 is only for providing 24V to the HCVR-SDU.
[10 empty] | 0.501 | <- max nac power threshold
[10 empty] | 0.1 | 0.236 | 0.136 | <- this calculates the amount of standby aux power remaining
[10 empty] | 0.62 | 2 | 1.38 | <- this calculates the amount of alarm power remaining (not used)
7
Calculation:
Standby | 0.1 | x | 24 | = | 2.4 |  | The maximum Standby current is 236mA.
Alarm | 0.62 | x | 0.083 | = | 0.05146 |  | The maximum HCVR-3 total current is 2 amps.
|  |  | Battery Size Required: |  | 2.4515 | Ah | The maximum battery size is 7Ah.
NOTE: Hochiki hereby disclaims all warranties relating to this software product, whether expressed or implied, including without
limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki cannot and will not be liable
for any incidental, consequential, special, indirect or similar damages for any reason. It is the responsibility of the user to
ascertain the accuracy and the reliability of any and all information generated or provided by this software.
Revision 1.02
Note on E21: Each HCVR-SDU requires 50mA in standby and 94mA in alarm.
Note on E22: Each HCVR-AB requires 16mA in standby and 175mA in alarm.
Note on E23: Each HCVR-SQA requires 6mA in standby and 900mA in alarm.
Note on K23: Because the SQA outputs are activated sequentially, the maximum alarm current will not exceed 0.9 amp at any time.