## EVAX Series
EVAX SYSTEMS
NOTE: NOT FOR DISTRIBUTION, FOR IN-HOUSE ONLY (SHEET STILL UNDER DEVELOPMENT)
Standard Product Line Battery Calc Worksheet
QTY | ITEM | STANDBY CURRENT |  | STANDBY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
| 100 / 100E | 0.18 | 0 | 24 | 0 | 1.2 | 0 | 0.25 | 0 | 0
| 50 / 50E | 0.15 | 0 | 24 | 0 | 0.8 | 0 | 0.25 | 0 | 0
| 25 / 25E | 0.18 | 0 | 24 | 0 | 1.1 | 0 | 0.25 | 0 | 0
| EVX-SC | 0.033 | 0 | 24 | 0 | 0.044 | 0 | 0.25 | 0 | 0
| EVX-RM | 0.033 | 0 | 24 | 0 | 0.044 | 0 | 0.25 | 0 | 0
| EVX-ZM | 0.051 | 0 | 24 | 0 | 0.13 | 0 | 0.25 | 0 | 0
| EVX-SL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| EVX-IL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| LED/switch | 0 | 0 | 24 | 0 | 0.01 | 0 | 0.25 | 0 | 0
| EVX-OL8 | 0.003 | 0 | 24 | 0 | 0.028 | 0 | 0.25 | 0 | 0
| EVX-ATM | 0.015 | 0 | 24 | 0 | 0.035 | 0 | 0.25 | 0 | 0
| EVX-BA | 0.04 | 0 | 24 | 0 | 0.01 | 0 | 0.25 | 0 | 0
| AL-600 | 0.1 | 0 |  |  | 0.1 | 0
0 | EVX-BAB |  | 0 | 0
|  | SUB TOTALS |  |  | 0 |  |  | SUB TOTAL (H) |  | 0
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.5
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 0
COLUMN
A |  | Total number of each item in each cabinet
C |  | Number of Hours for Standby Time
Typically: 24, or 60
D |  | Qty x Stand by Current x Stand-By Time = Total Stand-By Power, Column: A x B x C = D
Column: A x B x C = D
F |  | Alarm Time in hours is = to # of minutes / 60
example:15 min / 60 = .25 hours
G |  | Qty x Alarm Current x Alarm Time
Column: A x D x F = G
H |  | Total Stand-By Power + Total Alarm Power
Column: D + G = H
Formula: Total AH Power = Total COLUMN "H" x 1.2 (20% Safety Margin)
Total Amp Hour Power is the Amp Hour rating of each SET OF Batteries for EACH Amplifier
Calculation For: |  |  |  |  | Information: |  |  |  | Notes:
OEM / Distributor |  |  |  |  | Date: |  |  |  | batteries will require
Customer |  |  |  |  | Prepared By |  |  |  | external battery box
PO# |  |  |  |  | Fax To: |  |  |  | (not supplied by EVAX)
Job Name |  |  |  |  | Email To:
Panel:
Evax Systems hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Evax Systems cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason. It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.

## MNS (hidden)
Evax Systems
Battery Calc Worksheet
NOTE: NOT FOR DISTRIBUTION, FOR IN-HOUSE ONLY (SHEET STILL UNDER DEVELOPMENT)
EVAX 100M
QTY | ITEM | STANDBY CURRENT |  | STANDBY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
1 | 100 / 100E | 0.18 | 0.18 | 24 | 4.32 | 2.5 | 2.5 | 0.25 | 0.625 | 4.945
0 | EVX-RM8 | 0.012 | 0 | 24 | 0 | 0.037 | 0 | 0.25 | 0 | 0
1 | EVX-SL8 | 0.003 | 0.003 | 24 | 0.072 | 0.005 | 0.005 | 0.25 | 0.00125 | 0.07325
| EVX-IL8 | 0.003 | 0 | 24 | 0 | 0.005 | 0 | 0.25 | 0 | 0
| EVX-OL8 | 0.003 | 0 | 24 | 0 | 0.028 | 0 | 0.25 | 0 | 0
| EVX-ZM | 0.051 | 0 | 0 | 0 | 0.13 | 0 | 0 | 0 | 0
| AL-600 | 0.1 | 0 |  |  | 0.1 | 0
0 | EVX-BAB |  | 0 | 0
|  | SUB TOTALS |  |  | 4.392 |  |  | SUB TOTAL (H) |  | 5.0183
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.2
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 6.0219
COLUMN
A |  | Total number of each item in each cabinet
C |  | Number of Hours for Standby Time
Typically: 24, or 60
D |  | Qty x Stand by Current x Stand-By Time = Total Stand-By Power, Column: A x B x C = D
Column: A x B x C = D
F |  | Alarm Time in hours is = to # of minutes / 60
example:15 min / 60 = .25 hours
G |  | Qty x Alarm Current x Alarm Time
Column: A x D x F = G
H |  | Total Stand-By Power + Total Alarm Power
Column: D + G = H
Formula: Total AH Power = Total COLUMN "H" x 1.2 (20% Safety Margin)
Total Amp Hour Power is the Amp Hour rating of each SET OF Batteries for EACH Amplifier
Calculation For: |  |  |  |  | Information: |  |  |  | Notes:
OEM / Distributor |  |  |  |  | Date: |  |  |  | batteries will require
Customer |  |  |  |  | Prepared By |  |  |  | external battery box
PO# |  |  |  |  | Fax To: |  |  |  | (not supplied by EVAX)
Job Name |  |  |  |  | Email To:
Panel:
Evax Systems hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Evax Systems cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason.
It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.

## FNV MP
EVAX SYSTEMS HMX Master Panel Battery Calc Worksheet
NOTE: NOT FOR DISTRIBUTION, FOR IN-HOUSE ONLY (SHEET STILL UNDER DEVELOPMENT)
VoiceNET Master Panel Battery Calc Worksheet
QTY | ITEM | STANDBY CURRENT |  | STAND BY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
A |  | B |  | C |  | D |  | E
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
1 | FNV-SSC | 0.029 | 0.029 | 24 | 0.696 | 0.015 | 0.015 | 0.25 | 0.00375 | 0.69975
1 | FNV-MMC | 0.038 | 0.038 | 24 | 0.912 | 0.038 | 0.038 | 0.25 | 0.0095 | 0.9215
1 | FNV-ASC | 0.034 | 0.034 | 24 | 0.816 | 0.034 | 0.034 | 0.25 | 0.0085 | 0.8245
1 | FNV-DCC | 0.073 | 0.073 | 24 | 1.752 | 0.073 | 0.073 | 0.25 | 0.01825 | 1.7703
1 | FNV-PWR | 0.016 | 0.016 | 24 | 0.384 | 0.016 | 0.016 | 0.25 | 0.004 | 0.388
0 | AL-600 | 0.1 | 0 | 24 | 0 | 0.1 | 0 | 0.25 | 0 | 0
| FNV-SSC | 0.029 | 0 | 24 | 0 | 0.015 | 0 | 0.25 | 0 | 0
| FNV-SLC | 0.006 |  | 24 | 0 | 0.008 |  | 0.25 | 0 | 0
| FNV-FO | 0.051 | 0 | 24 | 0 | 0.051 | 0 | 0.25 | 0 | 0
| MX-FO7 | 0.04 | 0 | 24 | 0 | 0.04 | 0 | 0.25 | 0 | 0
| FNV-II | 0.019 | 0 | 24 | 0 | 0.03 | 0 | 0.25 | 0 | 0
| EVX-ATM | 0.015 | 0 | 24 | 0 | 0.035 | 0 | 0.25 | 0 | 0
| EVX-RM | 0.02 | 0 | 24 | 0 | 0.04 | 0 | 0.25 | 0 | 0
| EVX-SC | 0.03 | 0 | 24 | 0 | 0.05 | 0 | 0.25 | 0 | 0
| FNV-MFP | 0.022 | 0 | 24 | 0 | 0.032 | 0 | 0.25 | 0 | 0
0 | MX-MFH |  |  | 15 |  |  |  | 0
0 | MX-ISO | 0.02 | 0 | 15 | 0 | 0.02 | 0 | 0 | 0 | 0
0 | MX-ISO2 |  | 0 | 15 | 0 |  | 0 | 0 | 0 | 0
0 | MX-IPI |  | 0 | 15 | 0 |  | 0 | 0 | 0 | 0
0 | MX-KS4 |  | 0 | 15 | 0 |  | 0 | 0 | 0 | 0
|  | SUB TOTALS |  |  | 4.56 |  |  | SUB TOTAL (H) |  | 4.604
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.5
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 6.906
COLUMN
A |  | Total number of each item in each cabinet
C |  | Number of Hours for Stand By Time
Typically: 24, or 60
D |  | Qty x Stand by Current x Stand-By Time = Total Stand-By Power, Column: A x B x C = D
Column: A x B x C = D
F |  | Alarm Time in hours is = to # of minutes / 60
example:15 min / 60 = .25 hours
G |  | Qty x Alarm Current x Alarm Time
Column: A x D x F = G
H |  | Total Stand-By Power + Total Alarm Power
Column: D + G = H
Formula: Total AH Power = Total COLUMN "H" x 1.2 (20% Safety Margin)
Total Amp Hour Power is the Amp Hour rating of each SET OF Batteries for EACH Amplifier
Hochiki America hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki America cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason. It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.
Calculation For: |  |  |  |  | Information: |  |  |  | Notes:
OEM / Distributor |  |  |  |  | Date: |  |  |  | batteries will require
Customer |  |  |  |  | Prepared By |  |  |  | external battery box
PO# |  |  |  |  | Fax To: |  |  |  | (not supplied by EVAX)
Job Name |  |  |  |  | Email To:
Panel:

## FNV DP
Hochiki VoiceNET Distributed Panel Battery Calc Worksheet
NOTE: NOT FOR DISTRIBUTION, FOR IN-HOUSE ONLY (SHEET STILL UNDER DEVELOPMENT)
QTY | ITEM | STANDBY CURRENT |  | STAND BY TIME | TOTAL STANDBY PWR (AH) | ALARM CURRENT |  | ALARM TIME | TOTAL ALARM POWER | TOTAL Amp Hour POWER
A |  | B |  | C | D | E |  | F | G | H
A |  | B |  | C |  | D |  | E
|  |  |  | Hours | A x B x C |  |  | Hours | A x D x F | D + G
1 | FNV-AMI | 0.016 | 0.016 | 24 | 0.384 | 0.026 | 0.026 | 0.25 | 0.0065 | 0.3905
1 | FNV-MBK | 0.006 | 0.006 | 24 | 0.144 | 0.042 | 0.042 | 0.25 | 0.0105 | 0.1545
1 | FNV-MBR | 0.028 | 0.028 | 24 | 0.672 | 0.028 | 0.028 | 0.25 | 0.007 | 0.679
1 | FNV-DCC | 0.076 | 0.076 | 24 | 1.824 | 0.076 | 0.076 | 0.25 | 0.019 | 1.843
| FNV-MBK | 0.006 | 0 | 24 | 0 | 0.042 | 0 | 0.25 | 0 | 0
| EVX-100E | 0.18 | 0 | 24 | 0 | 2.5 | 0 | 0.25 | 0 | 0
| EVX-50E | 0.13 | 0 | 24 | 0 | 1 | 0 | 0.25 | 0 | 0
| EVX-25E | 0.18 | 0 | 24 | 0 | 1 | 0 | 0.25 | 0 | 0
| FNV-BA | 0.04 | 0 | 24 | 0 | 0.01 | 0 | 0.25 | 0 | 0
| EVX-BAB |  | 0 | 24 | 0 |  | 0 | 0.25 | 0 | 0
| EVX-ZAB | 0 | 0 | 24 | 0 | 0 | 0 | 0.25 | 0 | 0
| MX-INB |  | 0 | 24 | 0 |  | 0 | 0.25 | 0 | 0
| MX-AOR | 0.025 | 0 | 24 | 0 | 0.025 | 0 | 0.25 | 0 | 0
| MX-FPR |  | 0 | 24 | 0 |  | 0 | 0.25 | 0 | 0
| AL-600 | 0.1 | 0 | 24 | 0 | 0.1 | 0 | 0.25 | 0 | 0
| FNV-FO | 0.051 | 0 | 24 | 0 | 0.051 | 0 | 0.25 | 0 | 0
| FNV-FPI | 0.02 | 0 | 24 | 0 | 0.041 | 0 | 0.25 | 0 | 0
|  | SUB TOTALS |  |  | 3.024 |  |  | SUB TOTAL (H) |  | 3.067
| ENTER --- | Stby (hours) | 24 | 24 |  |  |  | Safety Factor 20% |  | 1.5
| ENTER --- | Alarm (mins) | 15 | 15
[6 empty] | Total Amp Hour Power |  |  |  | 4.6005
COLUMN
A |  | Total number of each item in each cabinet
C |  | Number of Hours for Stand By Time
Typically: 24, or 60
D |  | Qty x Stand by Current x Stand-By Time = Total Stand-By Power, Column: A x B x C = D
Column: A x B x C = D
F |  | Alarm Time in hours is = to # of minutes / 60
example:15 min / 60 = .25 hours
G |  | Qty x Alarm Current x Alarm Time
Column: A x D x F = G
H |  | Total Stand-By Power + Total Alarm Power
Column: D + G = H
Formula: Total AH Power = Total COLUMN "H" x 1.2 (20% Safety Margin)
Total Amp Hour Power is the Amp Hour rating of each SET OF Batteries for EACH Amplifier
Hochiki America hereby disclaims all warranties relating to this software utility, whether expressed or implied, including without limitations any implied warranties of merchantability or fitness for a particular purpose. Hochiki America cannot and will not be liable for any special, incidental, consequential, indirect or similar damages for any reason. It is the sole responsibility of the user to ascertain the accuracy and the reliability of any and all information generated or provided by this software utility.