## Sheet1
HCA Conventional Panel Battery Calculator Tool
The HCA Battery Calculator Tool will help you determine the batteries needed for your installation. In order to use this tool you must
know the number and type of devices that will be attached to your control panel, and the current requirements of any auxiliary devices
| being powered by the control panel. Please enter this information in the yellow boxes. | [5 empty] | To begin, answer the following questions… | [5 empty] | 0
[13 empty] | 20 | HCA-2
| How much Standby Time (in hours) is required for the installation? |  |  |  | 24 | Hours | [6 empty] | 0 | HCA-4
| How much Alarm Time* (in minutes) is required for the installation? |  |  |  | 5 | Minutes | [6 empty] | 1 | HCA-8
HCA-2D
| Which HCA model are you using? |  |  |  | HCA-2 | [8 empty] | HCA-4D
HCA-8D
| Panel Components |  | Comments |  |  |  |  | Total Standby Current |  | Total Alarm Current |  |  |  | 0.025
| HCA-2, HCA-4 or HCA-8 Panel | 1 | Fixed current draw for the 2, 4 or 8 zone panel |  |  |  |  | 0.16 |  | 0.29 |  |  | 24
| HCA Alarm Relay | 1 | Alarm relay only draws current when panel is in alarm |  |  |  |  | 0 |  | 0.025 |  |  | 48
| HCA Trouble Relay | 1 | Trouble relay does not draw current when running on battery |  |  |  |  | 0 |  | 0 |  |  | 60
| HCA Programmable Relay 1 |  | Programmable relay 1 only draws current for alarm |  |  |  |  | 0 |  | 0 |  |  | 72
| HCA Programmable Relay 2 |  | Programmable relay 2 only draws current for alarm |  |  |  |  | 0 |  | 0 |  |  | 90
| HCA Programmable Relay 3 |  | Programmable relay 3 only draws current for alarm |  |  |  |  | 0 |  | 0
| Remote Annunciator | [12 empty] | TRUE
| Number of HCA-RA | [6 empty] | 0 |  | 0
TRUE
| Detectors per Zone |  | Detector Quantity | Supervisory Current (uA) per Detector |  | Maximum Alarm Current (A)
| Number of Zone 1 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  | 5 | 0
| Number of Zone 2 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  | 15 | 0
| Number of Zone 3 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  | 20 | 0
| Number of Zone 4 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  | 30 | 0
| Number of Zone 5 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0
| Number of Zone 6 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  |  | 0
| Number of Zone 7 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  |  | 0
| Number of Zone 8 Detectors |  |  |  |  | 0.04 |  | 0 |  | 0 |  |  |  | 0
0
| Notification Appliances |  |  | Standby Current (A) (zero if NAC circuit) |  | Alarm Current (A)
| Output Circuit 1 Current | [6 empty] | 0 |  | 0
| Output Circuit 2 Current | [6 empty] | 0 |  | 0
| Output Circuit 3 Current | [6 empty] | 0 |  | 0
| Output Circuit 4 Current | [6 empty] | 0 |  | 0
0
| Total Standby/Alarm Current | [12 empty] | 0
[8 empty] | 0.16 | A | 0.315 | A
Site Information
| Total Standby Current Draw = |  | 0.16 | AMPS
| x Standby Time |  | 24 | Hours |  |  |  | Site Name-
| Standby Amp Hour Total = |  | 3.84 | AH |  |  |  | Address-
City-
| Total Alarm Current Draw = |  | 0.315 | AMPS |  |  |  | State & ZIP-
| x Alarm Time |  | 0.083333 | Hours*
| Alarm Amp Hour Total = |  | 0.02625 | AH |  |  |  | Phone-
| Standby Amp-Hours Required = |  | 3.84 | AH |  |  |  | Panel Info-
| Alarm Amp-Hours Required = |  | 0.02625 | AH
| Total AH Required= |  | 3.8662 | AH
| x Derating Factor |  | 1.2 | (20%)
| Minimum Battery Size Needed: |  | 4.6395 | AH
Install Date-
The HCA series panels can support batteries up to 18 AH.
| * 0.083 equals 5 minutes of alarm time, 0.25 equals 15 minutes of alarm. | [6 empty] | Misc.-
NOTE: Hochiki hereby disclaims all warranties relating to this software product, whether expressed or
implied. Including without limitations any implied warranties of merchantability or fitness for a
particular purpose. Hochiki cannot and will not be liable for any incidental, consequential, special,
indirect or similar damages for any reason. It is the responsibility of the user to ascertain the
accuracy and the reliability of any and all information generated or provided by this software.
[12 empty] | Rev. 2.01 | 0